{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["机组中温","机组低温","冷柜"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"机组中温","index":0,"n_rows":53,"n_cols":7,"rows_kept":53,"merged":[[0,0,0,6],[1,0,1,1],[1,2,1,3],[1,4,1,6],[2,0,2,2],[2,3,2,6],[3,0,3,1],[3,4,3,5],[4,0,9,0],[4,2,5,2],[4,3,5,3],[7,1,9,1],[7,2,9,2],[7,3,9,3],[10,0,43,0],[10,1,18,1],[10,2,18,2],[10,3,18,3],[10,6,12,6],[13,6,15,6],[16,6,18,6],[19,1,21,1],[19,2,21,2],[19,3,21,3],[22,1,24,1],[22,2,24,2],[22,3,24,3],[26,1,28,1],[31,1,39,1],[31,2,39,2],[31,3,39,3],[31,6,33,6],[34,6,36,6],[37,6,39,6],[40,1,42,1],[40,2,42,2],[40,3,42,3],[44,0,48,0],[44,1,46,1],[44,3,45,3],[44,6,45,6],[47,1,48,1],[49,0,51,0],[52,1,52,6]],"flags":["formulas_cached_only"]}
["维护巡检报告---机组点检表（中温）-附件2"]
["点检时间：",null,"点检技师：",null,"门店设备维护部："]
["机组品牌：",null,null,"机组型号："]
["保养检查项目",null,"点检方法","参考基准","实侧值",null,"判定与行动"]
["主电源回路","主电源回路绝缘测试 ","用500V绝缘计测量（确认切断电源后测量）","在10MΩ以上","记录","     MΩ"]
[null,"操作回路绝缘测试",null,null,"记录","     MΩ"]
[null,"电气线路检查","目视检查及用螺丝刀拧紧各端子","无松驰，无烧损，无变色","记录"]
[null,"主电源电压","用电压表测量","额定电压±10%以内，相间电压不均衡在±2%以内","A－B","       V"]
[{"$nulls":4},"A－C","       V"]
[{"$nulls":4},"B--C ","       V"]
["压      缩       机","压缩机绝缘测试","用500V绝缘计测量（确认切断电源后测量）","对地10MΩ以上","No1 R对地","    MΩ         "]
[{"$nulls":4},"No1 S对地","    MΩ         "]
[{"$nulls":4},"No1 T对地","    MΩ         "]
[{"$nulls":4},"No2 R对地","    MΩ         "]
[{"$nulls":4},"No2 S对地","    MΩ         "]
[{"$nulls":4},"No2 T对地","    MΩ         "]
[{"$nulls":4},"No3 R对地","    MΩ         "]
[{"$nulls":4},"No3 S对地","    MΩ         "]
[{"$nulls":4},"No3 T对地","    MΩ         "]
[null,"压缩机用电磁接触器（触点，线圈，衔铁，机械互锁）","目视检查及用螺丝刀拧紧各端子，清洁触点、线圈、衔铁等部件，检查机械互锁机构","接点无花，无松驰，无烧损线圈、衔铁、机械互锁机构等部件工作正常","No1"]
[{"$nulls":4},"No2"]
[{"$nulls":4},"No3"]
[null,"压缩机油位","目视检查","1/3--2/3","No1"]
[{"$nulls":4},"No2"]
[{"$nulls":4},"No3"]
[null,"油分离器油位与颜色","目视检查","不少于1/3，油质清","记录"]
[null,"系统冷媒量","目视检查","储液器不少于1/3","记录"]
[null,null,"目视检查","视液镜无气泡","记录"]
[null,null,"目视检查","视液镜试纸颜色（绿色或紫色）","记录"]
[null,"系统排出压力","参照压力表","根据机型确定","记录","    Mpa"]
[null,"系统吸入压力","参照压力表","根据机型确定","记录","    Mpa"]
[null,"运转电流","用钳表测定","额定工况下，100%负载运转时额定电流的115%以下","No1 R","        A"]
[{"$nulls":4},"No1 S","         A"]
[{"$nulls":4},"No1 T","        A"]
[{"$nulls":4},"No2 R","        A"]
[{"$nulls":4},"No2 S","        A"]
[{"$nulls":4},"No2 T","        A"]
[{"$nulls":4},"No3 R","        A"]
[{"$nulls":4},"No3 S","        A"]
[{"$nulls":4},"No3 T","        A"]
[null,"压缩机运行时间","检查运行记录","正常范围内","No1","H"]
[{"$nulls":4},"No2","H"]
[{"$nulls":4},"No3","H"]
[null,"压缩机噪音与振动","听觉","无异常噪音及振动","记录"]
["冷凝器","水冷式","入水温度","温差5℃适宜","入水","    ℃"]
[null,null,"出水温度",null,"出水","    ℃"]
[null,null,"水泵与风机运行情况","正常","记录"]
[null,"风冷式","风机运转","正常范围","记录"]
[null,null,"翅片洁净","洁净通风良好","记录"]
["其它","机房温度","用温度计测量","夏季不超过室外温度5℃","记录","℃"]
[null,"机组渗漏检修","检漏仪或肥皂水","无泄漏点","记录"]
[null,"外观状况","目视检查","无腐蚀，无损坏零件等","记录"]
["结论"]

{"sheet":"机组低温","index":1,"n_rows":53,"n_cols":7,"rows_kept":53,"merged":[[0,0,0,6],[1,0,1,1],[1,2,1,3],[1,4,1,6],[2,0,2,2],[2,3,2,6],[3,0,3,1],[3,4,3,5],[4,0,9,0],[4,2,5,2],[4,3,5,3],[7,1,9,1],[7,2,9,2],[7,3,9,3],[10,0,43,0],[10,1,18,1],[10,2,18,2],[10,3,18,3],[10,6,12,6],[13,6,15,6],[16,6,18,6],[19,1,21,1],[19,2,21,2],[19,3,21,3],[22,1,24,1],[22,2,24,2],[22,3,24,3],[26,1,28,1],[31,1,39,1],[31,2,39,2],[31,3,39,3],[31,6,33,6],[34,6,36,6],[37,6,39,6],[40,1,42,1],[40,2,42,2],[40,3,42,3],[44,0,48,0],[44,1,46,1],[44,3,45,3],[44,6,45,6],[47,1,48,1],[49,0,51,0],[52,1,52,6]],"flags":["formulas_cached_only"]}
["维护巡检报告---机组点检表（低温）-附件2"]
["点检时间：",null,"点检技师：",null,"门店设备维护部："]
["机组品牌：",null,null,"机组型号："]
["保养检查项目",null,"点检方法","参考基准","实侧值",null,"判定与行动"]
["主电源回路","主电源回路绝缘测试 ","用500V绝缘计测量（确认切断电源后测量）","在10MΩ以上","记录","     MΩ"]
[null,"操作回路绝缘测试",null,null,"记录","     MΩ"]
[null,"电气线路检查","目视检查及用螺丝刀拧紧各端子","无松驰，无烧损，无变色","记录"]
[null,"主电源电压","用电压表测量","额定电压±10%以内，相间电压不均衡在±2%以内","A－B","       V"]
[{"$nulls":4},"A－C","       V"]
[{"$nulls":4},"B--C ","       V"]
["压      缩       机","压缩机绝缘测试","用500V绝缘计测量（确认切断电源后测量）","对地10MΩ以上","No1 R对地","    MΩ         "]
[{"$nulls":4},"No1 S对地","    MΩ         "]
[{"$nulls":4},"No1 T对地","    MΩ         "]
[{"$nulls":4},"No2 R对地","    MΩ         "]
[{"$nulls":4},"No2 S对地","    MΩ         "]
[{"$nulls":4},"No2 T对地","    MΩ         "]
[{"$nulls":4},"No3 R对地","    MΩ         "]
[{"$nulls":4},"No3 S对地","    MΩ         "]
[{"$nulls":4},"No3 T对地","    MΩ         "]
[null,"压缩机用电磁接触器（触点，线圈，衔铁，机械互锁）","目视检查及用螺丝刀拧紧各端子，清洁触点、线圈、衔铁等部件，检查机械互锁机构","接点无花，无松驰，无烧损线圈、衔铁、机械互锁机构等部件工作正常","No1"]
[{"$nulls":4},"No2"]
[{"$nulls":4},"No3"]
[null,"压缩机油位","目视检查","1/3--2/3","No1"]
[{"$nulls":4},"No2"]
[{"$nulls":4},"No3"]
[null,"油分离器油位与颜色","目视检查","不少于1/3，油质清","记录"]
[null,"系统冷媒量","目视检查","储液器不少于1/3","记录"]
[null,null,"目视检查","视液镜无气泡","记录"]
[null,null,"目视检查","视液镜试纸颜色（绿色或紫色）","记录"]
[null,"系统排出压力","参照压力表","根据机型确定","记录","    Mpa"]
[null,"系统吸入压力","参照压力表","根据机型确定","记录","    Mpa"]
[null,"运转电流","用钳表测定","额定工况下，100%负载运转时额定电流的115%以下","No1 R","        A"]
[{"$nulls":4},"No1 S","         A"]
[{"$nulls":4},"No1 T","        A"]
[{"$nulls":4},"No2 R","        A"]
[{"$nulls":4},"No2 S","        A"]
[{"$nulls":4},"No2 T","        A"]
[{"$nulls":4},"No3 R","        A"]
[{"$nulls":4},"No3 S","        A"]
[{"$nulls":4},"No3 T","        A"]
[null,"压缩机运行时间","检查运行记录","正常范围内","No1","H"]
[{"$nulls":4},"No2","H"]
[{"$nulls":4},"No3","H"]
[null,"压缩机噪音与振动","听觉","无异常噪音及振动","记录"]
["冷凝器","水冷式","入水温度","温差5℃适宜","入水","    ℃"]
[null,null,"出水温度",null,"出水","    ℃"]
[null,null,"水泵与风机运行情况","正常","记录"]
[null,"风冷式","风机运转","正常范围","记录"]
[null,null,"翅片洁净","洁净通风良好","记录"]
["其它","机房温度","用温度计测量","夏季不超过室外温度5℃","记录","℃"]
[null,"机组渗漏检修","检漏仪或肥皂水","无泄漏点","记录"]
[null,"外观状况","目视检查","无腐蚀，无损坏零件等","记录"]
["结论"]

{"sheet":"冷柜","index":2,"n_rows":27,"n_cols":12,"rows_kept":27,"merged":[[0,0,2,11],[3,0,3,1],[3,2,3,5],[3,6,3,8],[3,10,3,11],[4,0,4,1],[4,8,4,11],[20,2,20,3],[20,4,20,5],[20,7,20,8],[20,10,20,11],[22,2,22,3],[22,4,22,5],[22,7,22,8],[22,10,22,11],[24,2,24,3],[24,4,24,5],[24,7,24,8],[24,10,24,11],[25,1,25,9],[26,1,26,9]],"flags":["formulas_cached_only"]}
["维护巡检报告---冷柜和机组部分-附件2"]
[]
[]
["客户名称：",null,"地址：",{"$nulls":3},"    年    月   日",null,null,"环境温湿度：  ℃ ，RH   %","保养人："]
["展示柜型号",{"$nulls":7},"机 组 部 分"]
["序号","检查项目","柜 1","柜 2 ","柜 3","柜 4","柜 5","柜 6","序号","检查项目","中温机组","低温机组"]
[1,"环境温度","     ℃","     ℃","     ℃","     ℃","     ℃","     ℃",1,"电压（380V±10%）相间不平衡2%","/  /","/  /"]
[2,"环境湿度","RH","     RH","RH","RH","RH ","RH",2,"压缩机运行电流","/  /","/  /"]
[3,"设定温度","     ℃","     ℃","     ℃","     ℃","     ℃","     ℃",3,"冷凝器是否需要清洗"]
[4,"外界是否有风源影响风幕","是  否","是  否","是  否","是  否","是  否","是  否",4,"高压","bar","bar"]
[5,"化霜方式 电/自然",{"$nulls":6},5,"低压","bar","bar"]
[6,"化霜加热管电流","      A","      A","      A","      A","      A","      A",6,"管路有无异常噪音或者震动"]
[7,"化霜终止温度",{"$nulls":6},7,"冷凝风机是否正常"]
[8,"排水是否畅通","是  否","是  否","是  否","是  否","是  否","是  否",8,"制冷剂在储液器中的液位(1/2  无)"]
[9,"蒸发器是否有霜堵",{"$nulls":6},9,"压缩机停机压力"]
[10,"电器端子压线是否牢固","是  否","是  否","是  否","是  否","是  否","是  否",10,"电器盒内端子压线是否牢固烧焦"]
[11,"线路是否有破皮烧焦","是  否","是  否","是  否","是  否","是  否","是  否",11,"压缩机油位(1/8   3/8   1/2)"]
[12,"电磁阀是否固定",{"$nulls":6},12,"压缩机油的颜色(发黑  清澈  发黄)  "]
[13,"商品堆放是否影响风幕","是  否","是  否","是  否","是  否","是  否","是  否",13,"管路是否有油痕迹"]
[14,"柜内管路是否有震动摩擦",{"$nulls":6},14,"视液镜 （发黄  发绿   吹气泡）"]
[null,"客户满意度","非常满意",null,"满意",null,"一般","  不满意",null,"备注说明：","维保人员签字："]
[]
[null,"服务态度","¨",null,"¨",null,"¨","¨",null,null,"客户签字："]
[]
[null,"保养质量","¨",null,"¨",null,"¨","¨",null,null,"联系电话:"]
[null,"填写要求：1.按照公司的维保要求必须严格执行，填写内容必须属实"]
[null,"          2.每次保养完成后维保人员在维保单上签字，并让门店相关人员签字确认"]